## Fire Alarm
BOQ of Fire Alarm
Sl. | Name of the Item | Specification | Required Quantity | Unit Measurement | Unit Price | Total Price
[5 empty] | (Estimated) | (Estimated)
[5 empty] | BDT | BDT
1 | Analogue addressable fire alarm control panel 1(One) | Loop Panel addressable fire alarm control panel with optional Digital Alarm Communicator/Transmitter (DACT-UD2) Auto programmable function Advanced Fire Technology includes sensitivity testing and automatic drift compensation 7 amps of power distributed across 4 NAC Display: LCD display, Power supply: 220/50 VAC Brand: Tyco, simplex, Origin:USA Model:4100ES, Approval:UL,FM,CSFM,MEA,ULC Approved | 1 | Set
2 | Addressable smoke detector | Microprocessor based addressable Smoke Detector. Detector sensitivity must be programmed in the control panel software. Sensitivity must be continuously monitored and reported to the panel. Approvals: UL Listed. Brand: Tyco, simplex Origin:USA Approval:UL,FM,CSFM,MEA,ULC Approved Model: 4098-9714,4098-9789 | 54 | Nos
3 | Addressable Heat Detector with Base | Addressable Microprocessor based Rate of rise cum fixed temperature detector with mounting based LED, address switch to program the detectors complete as required. UL Listed & FM Approved Model: 4098-9733,4098-9789 | 11 | Nos
4 | Addressable Fault Isolator Module | Fault isolator module is used to protect the system against wire-to-wire short circuits on the loop. The modules should be spaced between groups of sensors or modules in a loop to protect the rest of the loop. In the event of a short circuit between any two fault isolator modules, both modules immediately switch to an open circuit condition and isolate any group of sensors between them. The remaining units on the circuit will continue to operate in a normal fashion (must be wired in class 'A' or Style 6) A maximum load of 25 devices can be connected to an isolator to insure that the isolator powers up correctly. Model: 4090-9116,Brand: Tyco, simplexOrigin:USA ,Approval:UL,FM,CSFM,MEA,ULC | 5 | Nos
5 | Addressable Manual call point | Supply and installation of addressable type manual double action pull station complete with back box and all other accessories and consumables. Power supply shall be 24V DC. Confirming requirements NFPA 72 and according to UL listed. Brand: Tyco, simplex Origin:USA Model: 4099-9006 Approval: UL,FM,CSFM,MEA,ULC | 5 | Nos
6 | Addressable Hooter cum Strobe | Horn with Strobe for Audible & Visible application, combination of Audible & Visible (A/V) Notification Appliances shall be listed to UL 1971 and UL 464, LPCB. UL Listed & FM Approved Model: 49AV-WRF | 7 | Nos
7 | FRLS 2x1.5 rm Cable | Brand: BRB/BBS/Macro or Equivalent | 650 | RM
8 | FRLS 2x2.5 rm Cable | Brand: BRB/BBS/Macro or Equivalent | 300 | RM
9 | Fire Cable Conduitsize:20mm | Brand: Bashundhara or Equivalent | 1 | Lot
10 | PVC Elbow, TEE, junction box, ETC | Brand: Bashundhara or Equivalent | 1 | Lot
11 | Installation,Testing,Commissioning and Balancing | After proper installation and certification the system shall be tested, commissioned and balanced as per direction and recommendation by the Manufacturer as well as Designer. | 1 | Lot
| Total Amount: |  |  |  |  | 0
Grand Total

## Steel Stair
BOQ of Steel Stair
Sl. | Name of the Item | Specification | Required Quantity | Unit Measurement | Unit Price | Total Price
[5 empty] | (Estimated) | (Estimated)
[5 empty] | BDT | BDT
1 | NS I Beam | 300 mmx 175 mm | 175 | Rft
2 | C- Channel | 150 mmx 75 mmx5mm | 1006 | KG
3 | Angle | 50 mmx 50 mmx4mm | 500 | KG
4 | Clecker Plate | 4mm | 1600 | KG
5 | Da φ 2" SS ipe | 1.5 mm | 551 | Rft
6 | Da φ 1" SS ipe | 1.5 mm | 200 | Rft
7 | 6mm thickness base plate | 8'x8' | 15 | KG
8 | Q45mm thick color profile sheet for root sheeting
9 | Paint | Red Oxide primary coat
10 | Erection & Fabrication
11 | Ancor Bolt
12 | Transport Cost
|  |  | Total Taka |  |  | 0
13 | Sand |  | 200 | CFT
14 | Sand Filling |  | 400 | CFT
15 | Brick |  | 3100 | Pcs
16 | Site Preparation |  |  | Job
17 | Cement |  | 50 | Bag
18 | Rod φ 10 & 16 mm |  | 280 | KG
19 | Brick Chips |  | 200 | CFT
20 | Transport Cost |  |  | Jnos
21 | Labour Cost |  |  | Nos
22 | others expenditure |  |  | Nos
23 | Earth Cutting & Fillng
[5 empty] | Total Taka | 0
Final Total=